## Slide 1
Distribution system expansion planning optimization

## Slide 2: Optimization objective and strategy
We start from a traditional approach:
  Centralized point of view
  Investment in substation and conductors
  Minimization of the yearly cost given by:
    amortized investment + operational cost
  Subject to Power Flow equation together with budget and topology constraint

## Slide 3: Investment options
HV sub
MV sub
MV load
LV load
  Two voltage levels each with its own substations.
  Their locations are optimized from a set of candidates

## Slide 4: Physical model
We start from Distflow with conic relaxation
We proceed by linearizing the conic constraint:
  Complex power (voltage assumed = 1 p.u.)
  Substation limits

## Slide 5: Substation limit linearization
 | CONIC | INT 8 | INT 16 | EXT 8 | EXT 16
HV capacity | 121.728 | 131.714 | 124.077 | 121.712 | 121.692

## Slide 6: Power linearization

## Slide 7: Power flow validation
To validate the proposed solution, we compare the operating points computed by the optimization with a complete AC power flow. To do so we build on panda power the proposed net.

## Slide 8
Conic constraint

## Slide 9
10 block linearized constraint

## Slide 10
15 block linearized constraint

## Slide 11: PV integration
Integration of Renewable Energy Sources (RES)
  PV is the only option considered.
  Maximum installation depends on building surface
  Two distinct investment PV & Inverter
  Linearized capability curve

## Slide 12: Visual function for dynamic plotting

## Slide 13: Multistage approach
Assumptions:
Addition of fixed installation costs
Capacities of substations and PV are strictly increasing
Conductors costs must be defined to separate new installation and reconductoring
Backward propagation of stages

## Slide 14: Topology update and storage
Fictitious Power for network topolgy
Vincoli di radialità graph based??
Implementation of storage
 Tuning of Gurobi parameters

## Slide 15: Representative days and increased load
Representative days
Load curve for increased consumption and EV +EHP adoption
Modified storage logic (No soc variation between start and end of day)
Tolleranza sui limiti storage (disugualianza)
Modified cost function with RD weights

## Slide 16: Updates
Fixes:
Identified some bugs caused by tolerances  Storage needs fixing
Optimization is getting stuck around 1% gap  Why? Is the storage?
Goals:
Analysis of power-flow results in critical conditions
Improving load curves
Rescaling  Is it necessary?
Efficiencies on storage  I need P_charge & P_discharge

## Slide 17: Updates
Single hybrid inverter
. DC bus between PV & Storage
. Inverter can inject reactive power
Reactive power should have a cost  Literature around 2€/MVAr  Every bus has PV +inverter but the oversizeing is greater at critical buses

## Slide 18: Analysis of load data

## Slide 19: Full campus intractability
The problem is too big to solve on a full campus!
I can fix the best conductor 
Minimum spanning tree is forced to connect every substation

## Slide 20: Next steps
Starting from obtained topology and line loading try to downgrade conductors
Dividing problem by district
Dividing MV and LV problems
Obtaining a gap with respect to the full problem